# Status Report: Controls Retrofit Commissioning

Status: on track, one watch item. Functional testing for Vazquez, Sanchez and Gutierrez is complete across all eight air handlers and the chilled-water plant; the issues log stands at 47 raised, 44 closed. Seasonal verification remains scheduled inside the engagement term. Prepared by Jeff Fowler.

## Completed this period

Closed functional testing on the final two air handlers after the combined test day, including the retest allowance.

Completed the two-week post-acceptance trend review; John Johnson's issues log drove three contractor fixes, all verified in trends.

Issue 41 (overnight setpoint) closed: failed damper actuator replaced and verified across five consecutive nights.

## Watch item

Three issues remain open, all documentation: as-built sequences and the point database export. None block occupancy or the seasonal test, but final acceptance should not be signed until they close.

## Budget

The engagement remains within the agreed fixed fee of $116,500, invoiced monthly per the engagement letter. Both allowed retest days were used; no additional scope has been requested.